## Tags Out
Name | Data Type | Value | Comment
DI_SYS_bEmergencyStop | Bool | 1 | SYS. Emergency stop
DI_SYS_bFaultReset | Bool | 0 | SYS. Fault reset command
DI_SYS_bFire | Bool | 1 | SYS. Fire alarm
DI_SYS_bStart | Bool | 1 | SYS. Start command
DI_SYS_bStop | Bool | 0 | SYS. Stop command
DI_SYS_bVoltageOk | Bool | 1 | SYS. Voltage control
AI_iPT101 | Int | 5530 | PT-101. Pressure. Raw input
AI_iPT102 | Int | 5530 | PT-102. Pressure. Raw input
AI_iPT201 | Int | 5530 | PT-201. Pressure. Raw input
AI_iPT202 | Int | 5530 | PT-202. Pressure. Raw input
AI_iTT101 | Int | 5530 | TT-101. Temperature. Raw input
AI_iTT102 | Int | 5530 | TT-102. Temperature. Raw input
AI_iTT201 | Int | 5530 | TT-201. Temperature. Raw input
AI_iTT202 | Int | 5530 | TT-202. Temperature. Raw input
DI_P3101A_bLocalMode | Bool | 0 | P-3101A. Local mode
DI_P3101A_bRemoteMode | Bool | 0 | P-3101A. Remote mode
DI_P3101A_bRunning | Bool | 0 | P-3101A. Running
DI_P3101B_bLocalMode | Bool | 0 | P-3101B. Local mode
DI_P3101B_bRemoteMode | Bool | 0 | P-3101B. Remote mode
DI_P3101B_bRunning | Bool | 0 | P-3101B. Running
DI_P4101A_bLocalMode | Bool | 0 | P-4101A. Local mode
DI_P4101A_bRemoteMode | Bool | 0 | P-4101A. Remote mode
DI_P4101A_bRunning | Bool | 0 | P-4101A. Running
DI_P4101A_bVFDFault | Bool | 0 | P-4101A. VFD fault
DI_P4101B_bLocalMode | Bool | 0 | P-4101B. Local mode
DI_P4101B_bRemoteMode | Bool | 0 | P-4101B. Remote mode
DI_P4101B_bRunning | Bool | 0 | P-4101B. Running
DI_P4101B_bVFDFault | Bool | 0 | P-4101B. VFD fault
DI_TCV101_bClosed | Bool | 1 | TCV-101. Closed position
DI_TCV101_bLocalMode | Bool | 0 | TCV-101. Local mode
DI_TCV101_bOpen | Bool | 0 | TCV-101. Open position
DI_TCV101_bRemoteMode | Bool | 0 | TCV-101. Remote mode
DI_TCV201_bClosed | Bool | 1 | TCV-201. Closed position
DI_TCV201_bLocalMode | Bool | 0 | TCV-201. Local mode
DI_TCV201_bOpen | Bool | 0 | TCV-201. Open position
DI_TCV201_bRemoteMode | Bool | 0 | TCV-201. Remote mode

## Tags In
Name | Data Type | Comment
DQ_P3101A_bStart | Bool | P-3101A. Start command
DQ_P3101B_bStart | Bool | P-3101B. Start command
DQ_P4101A_bStart | Bool | P-4101A. Start command
DQ_P4101B_bStart | Bool | P-4101B. Start command
DQ_SYS_bFault | Bool | SYS. Fault
DQ_SYS_bHorn | Bool | SYS. Audible alarm
DQ_SYS_bRunning | Bool | SYS. Running
DQ_TCV101_bClose | Bool | TCV-101. Close command
DQ_TCV101_bOpen | Bool | TCV-101. Open command
DQ_TCV201_bClose | Bool | TCV-201. Close command
DQ_TCV201_bOpen | Bool | TCV-201. Open command
DQ_XV201_bOpen | Bool | XV-201. Open command

## Sensor
Name | Tag | Value | Min | Max | Period | Comment
PT101 | AI_iPT101 | 5530 | 5530 | 27648 | 5 | PT-101. Pressure
PT102 | AI_iPT102 | 5530 | 5530 | 27648 | 5 | PT-102. Pressure
PT201 | AI_iPT201 | 5530 | 5530 | 27648 | 5 | PT-201. Pressure
PT202 | AI_iPT202 | 5530 | 5530 | 27648 | 5 | PT-202. Pressure
TT101 | AI_iTT101 | 5530 | 5530 | 27648 | 5 | TT-101. Temperature
TT102 | AI_iTT102 | 5530 | 5530 | 27648 | 5 | TT-102. Temperature
TT201 | AI_iTT201 | 5530 | 5530 | 27648 | 5 | TT-201. Temperature
TT202 | AI_iTT202 | 5530 | 5530 | 27648 | 5 | TT-202. Temperature

## Engine
Name | Start Tag | State Tag | Local Control Tag | Remote Control Tag | Runap Time | Cooldown Time | Comment
P3101A | DQ_P3101A_bStart | DI_P3101A_bRunning | DI_P3101A_bLocalMode | DI_P3101A_bRemoteMode | 2 | 1 | P-3101A. Start command
P3101B | DQ_P3101B_bStart | DI_P3101B_bRunning | DI_P3101B_bLocalMode | DI_P3101B_bRemoteMode | 2 | 1 | P-3101B. Start command
P4101A | DQ_P4101A_bStart | DI_P4101A_bRunning | DI_P4101A_bLocalMode | DI_P4101A_bRemoteMode | 2 | 1 | P-4101A. Start command
P4101B | DQ_P4101B_bStart | DI_P4101B_bRunning | DI_P4101B_bLocalMode | DI_P4101B_bRemoteMode | 2 | 1 | P-4101B. Start command

## Valve
Name | Opened Tag | Closed Tag | Open Tag | Close Tag | Local Control Tag | Remote Control Tag | Full Time | Comment
TCV101 | DI_TCV101_bOpen | DI_TCV101_bClosed | DQ_TCV101_bOpen | DQ_TCV101_bClose | DI_TCV101_bLocalMode | DI_TCV101_bRemoteMode | 10 | TCV-101. Open command
TCV201 | DI_TCV201_bOpen | DI_TCV201_bClosed | DQ_TCV201_bOpen | DQ_TCV201_bClose | DI_TCV201_bLocalMode | DI_TCV201_bRemoteMode | 10 | TCV-201. Open command
XV201 | None | None | DQ_XV201_bOpen | None | None | None | 10 | XV-201. Open command

## Delay
Name | Start Tag | State Tag | Delay | Comment

## Scenario
Object | Method | Tag | Value | Comment
h | log |  |  | Generated smoke scenario: Sensor / Engine / Valve only. Tags are initialized from configuration.
h | wait |  | 2 | Initial stabilization after tag initialization
// Component Sensors: Sensor smoke
// Sensor PT101
PT101 | sin |  |  | PT101: sinusoidal raw signal
h | wait |  | 10 | PT101: wait sinusoidal signal
PT101 | const |  | 0 | PT101: raw zero / fault simulation
h | wait |  | 5 | PT101: wait raw zero
PT101 | const |  | 5530 | PT101: return to zero point
h | wait |  | 5 | PT101: wait restored zero point
h | confirm |  |  | PT101: restored to zero point, sensor fault should be cleared
// Sensor PT102
PT102 | sin |  |  | PT102: sinusoidal raw signal
h | wait |  | 10 | PT102: wait sinusoidal signal
PT102 | const |  | 0 | PT102: raw zero / fault simulation
h | wait |  | 5 | PT102: wait raw zero
PT102 | const |  | 5530 | PT102: return to zero point
h | wait |  | 5 | PT102: wait restored zero point
h | confirm |  |  | PT102: restored to zero point, sensor fault should be cleared
// Sensor PT201
PT201 | sin |  |  | PT201: sinusoidal raw signal
h | wait |  | 10 | PT201: wait sinusoidal signal
PT201 | const |  | 0 | PT201: raw zero / fault simulation
h | wait |  | 5 | PT201: wait raw zero
PT201 | const |  | 5530 | PT201: return to zero point
h | wait |  | 5 | PT201: wait restored zero point
h | confirm |  |  | PT201: restored to zero point, sensor fault should be cleared
// Sensor PT202
PT202 | sin |  |  | PT202: sinusoidal raw signal
h | wait |  | 10 | PT202: wait sinusoidal signal
PT202 | const |  | 0 | PT202: raw zero / fault simulation
h | wait |  | 5 | PT202: wait raw zero
PT202 | const |  | 5530 | PT202: return to zero point
h | wait |  | 5 | PT202: wait restored zero point
h | confirm |  |  | PT202: restored to zero point, sensor fault should be cleared
// Sensor TT101
TT101 | sin |  |  | TT101: sinusoidal raw signal
h | wait |  | 10 | TT101: wait sinusoidal signal
TT101 | const |  | 0 | TT101: raw zero / fault simulation
h | wait |  | 5 | TT101: wait raw zero
TT101 | const |  | 5530 | TT101: return to zero point
h | wait |  | 5 | TT101: wait restored zero point
h | confirm |  |  | TT101: restored to zero point, sensor fault should be cleared
// Sensor TT102
TT102 | sin |  |  | TT102: sinusoidal raw signal
h | wait |  | 10 | TT102: wait sinusoidal signal
TT102 | const |  | 0 | TT102: raw zero / fault simulation
h | wait |  | 5 | TT102: wait raw zero
TT102 | const |  | 5530 | TT102: return to zero point
h | wait |  | 5 | TT102: wait restored zero point
h | confirm |  |  | TT102: restored to zero point, sensor fault should be cleared
// Sensor TT201
TT201 | sin |  |  | TT201: sinusoidal raw signal
h | wait |  | 10 | TT201: wait sinusoidal signal
TT201 | const |  | 0 | TT201: raw zero / fault simulation
h | wait |  | 5 | TT201: wait raw zero
TT201 | const |  | 5530 | TT201: return to zero point
h | wait |  | 5 | TT201: wait restored zero point
h | confirm |  |  | TT201: restored to zero point, sensor fault should be cleared
// Sensor TT202
TT202 | sin |  |  | TT202: sinusoidal raw signal
h | wait |  | 10 | TT202: wait sinusoidal signal
TT202 | const |  | 0 | TT202: raw zero / fault simulation
h | wait |  | 5 | TT202: wait raw zero
TT202 | const |  | 5530 | TT202: return to zero point
h | wait |  | 5 | TT202: wait restored zero point
h | confirm |  |  | TT202: restored to zero point, sensor fault should be cleared
// Component P3101: Engine smoke
// Engine P3101A
P3101A | mode_off |  |  | P3101A: off mode
h | wait |  | 2 | P3101A: wait off mode
P3101A | mode_local |  |  | P3101A: local mode
h | wait |  | 2 | P3101A: wait local mode
P3101A | mode_remote |  |  | P3101A: remote mode
h | wait |  | 2 | P3101A: wait remote mode
P3101A | start_fail |  |  | P3101A: start feedback disabled, non-start simulation
h | wait |  | 5 | P3101A: wait non-start window
P3101A | start_normal |  |  | P3101A: normal start feedback enabled
h | wait |  | 5 | P3101A: wait normal mode
h | confirm |  |  | P3101A: simulator is in normal remote mode; manual/auto start-stop can be tested from HMI
// Engine P3101B
P3101B | mode_off |  |  | P3101B: off mode
h | wait |  | 2 | P3101B: wait off mode
P3101B | mode_local |  |  | P3101B: local mode
h | wait |  | 2 | P3101B: wait local mode
P3101B | mode_remote |  |  | P3101B: remote mode
h | wait |  | 2 | P3101B: wait remote mode
P3101B | start_fail |  |  | P3101B: start feedback disabled, non-start simulation
h | wait |  | 5 | P3101B: wait non-start window
P3101B | start_normal |  |  | P3101B: normal start feedback enabled
h | wait |  | 5 | P3101B: wait normal mode
h | confirm |  |  | P3101B: simulator is in normal remote mode; manual/auto start-stop can be tested from HMI
// Component P4101: Engine smoke
// Engine P4101A
P4101A | mode_off |  |  | P4101A: off mode
h | wait |  | 2 | P4101A: wait off mode
P4101A | mode_local |  |  | P4101A: local mode
h | wait |  | 2 | P4101A: wait local mode
P4101A | mode_remote |  |  | P4101A: remote mode
h | wait |  | 2 | P4101A: wait remote mode
P4101A | start_fail |  |  | P4101A: start feedback disabled, non-start simulation
h | wait |  | 5 | P4101A: wait non-start window
P4101A | start_normal |  |  | P4101A: normal start feedback enabled
h | wait |  | 5 | P4101A: wait normal mode
h | confirm |  |  | P4101A: simulator is in normal remote mode; manual/auto start-stop can be tested from HMI
// Engine P4101B
P4101B | mode_off |  |  | P4101B: off mode
h | wait |  | 2 | P4101B: wait off mode
P4101B | mode_local |  |  | P4101B: local mode
h | wait |  | 2 | P4101B: wait local mode
P4101B | mode_remote |  |  | P4101B: remote mode
h | wait |  | 2 | P4101B: wait remote mode
P4101B | start_fail |  |  | P4101B: start feedback disabled, non-start simulation
h | wait |  | 5 | P4101B: wait non-start window
P4101B | start_normal |  |  | P4101B: normal start feedback enabled
h | wait |  | 5 | P4101B: wait normal mode
h | confirm |  |  | P4101B: simulator is in normal remote mode; manual/auto start-stop can be tested from HMI
// Component TCV: Valve smoke
// Valve TCV101
TCV101 | mode_off |  |  | TCV101: off mode
h | wait |  | 2 | TCV101: wait off mode
TCV101 | mode_local |  |  | TCV101: local mode
h | wait |  | 2 | TCV101: wait local mode
TCV101 | mode_remote |  |  | TCV101: remote mode
h | wait |  | 2 | TCV101: wait remote mode
TCV101 | fail |  |  | TCV101: feedback disabled, failure simulation
h | wait |  | 5 | TCV101: wait failure simulation
TCV101 | normal |  |  | TCV101: normal open/close feedback enabled
h | wait |  | 5 | TCV101: wait normal mode
h | confirm |  |  | TCV101: simulator is in normal remote mode; open/close can be tested from HMI
// Valve TCV201
TCV201 | mode_off |  |  | TCV201: off mode
h | wait |  | 2 | TCV201: wait off mode
TCV201 | mode_local |  |  | TCV201: local mode
h | wait |  | 2 | TCV201: wait local mode
TCV201 | mode_remote |  |  | TCV201: remote mode
h | wait |  | 2 | TCV201: wait remote mode
TCV201 | fail |  |  | TCV201: feedback disabled, failure simulation
h | wait |  | 5 | TCV201: wait failure simulation
TCV201 | normal |  |  | TCV201: normal open/close feedback enabled
h | wait |  | 5 | TCV201: wait normal mode
h | confirm |  |  | TCV201: simulator is in normal remote mode; open/close can be tested from HMI
// Component XV201: Valve smoke
// Valve XV201
XV201 | mode_off |  |  | XV201: off mode
h | wait |  | 2 | XV201: wait off mode
XV201 | mode_local |  |  | XV201: local mode
h | wait |  | 2 | XV201: wait local mode
XV201 | mode_remote |  |  | XV201: remote mode
h | wait |  | 2 | XV201: wait remote mode
XV201 | fail |  |  | XV201: feedback disabled, failure simulation
h | wait |  | 5 | XV201: wait failure simulation
XV201 | normal |  |  | XV201: normal open/close feedback enabled
h | wait |  | 5 | XV201: wait normal mode
h | confirm |  |  | XV201: simulator is in normal remote mode; open/close can be tested from HMI